## ORC Toluene
ORC TOLUENE
| PB main results |  | Cooling system main results
| Power generated (MW) | 101.052 | Thermal power dissiped (MW) | 149.2655
| Thermal Power required (MW) | 250.3175 | Fan power consume (MW) | 6.7426
| efficiency (%) | 40.3695 | Air mass flow rate (kg/s) | 21187.3746
| T_1 (ºC) | 35 | Cooler UA factor (MW/K) | 25.5761
| T_2 (ºC) | 36.4092 | Air inlet temperature (ºC) | 25
| T_3 (ºC) | 176.6058 | Air outlet temperature (ºC) | 32
T_3p (ºC)
| T_4 (ºC) | 391
| T_5 (ºC) | 219.4907
| T_6 (ºC) | 36.4092
| T_7 (ºC) | 0.062439
| P_1 (bar) | 46.8295
| P_2 (bar) | 46.8295
| P_3 (bar) | 46.8295
| P_4 (bar) | 45.8929
| P_5 (bar) | 0.065726
| P_6 (bar) | 0.062439
P_7(bar)
| Power cycle mas flow rate (kg/s) | 365.3023
| bypassing factor | 0
| UA recuperator (MW/K) | 42.9144
| UA SSG (MW/K) | 7.5009

## HRB Propane
HRB PROPANE
| PB main results |  | Cooling system main results
| Power generated (MW) | 100.28 | Thermal power dissiped (MW) | 150.0416
| Thermal Power required (MW) | 250.3175 | Fan power consume (MW) | 6.7776
| efficiency (%) | 40.0595 | Air mass flow rate (kg/s) | 21297.5395
| T_1 (ºC) | 35 | Cooler UA factor (MW/K) | 25.8066
| T_2 (ºC) | 48.0933 | Air inlet temperature (ºC) | 25
| T_3 (ºC) | 257.3744 | Air outlet temperature (ºC) | 32
| T_3p (ºC) | 243.8112
| T_4 (ºC) | 377
| T_5 (ºC) | 262.5754
| T_6 (ºC) | 54.592
| T_7 (ºC) | 203.329
| P_1 (bar) | 12.1788
| P_2 (bar) | 182.6825
| P_3 (bar) | 182.6825
| P_4 (bar) | 179.0288
| P_5 (bar) | 12.8198
| P_6 (bar) | 12.1788
| P_7(bar) | 12.1788
| Power cycle mas flow rate (kg/s) | 557.6741
| bypassing factor | 0.25
| UA recuperator (MW/K) | 45.755
| UA SSG (MW/K) | 7.9113

## HRB Isobutane
HRB ISOBUTANE
| PB main results |  | Cooling system main results
| Power generated (MW) | 88.4618 | Thermal power dissiped (MW) | 161.8556
| Thermal Power required (MW) | 250.3175 | Fan power consume (MW) | 7.3113
| efficiency (%) | 35.3399 | Air mass flow rate (kg/s) | 22974.4705
| T_1 (ºC) | 35 | Cooler UA factor (MW/K) | 26.2632
| T_2 (ºC) | 40.3267 | Air inlet temperature (ºC) | 25
| T_3 (ºC) | 201.7574 | Air outlet temperature (ºC) | 32
| T_3p (ºC) | 197.6484
| T_4 (ºC) | 308.85
| T_5 (ºC) | 213.0501
| T_6 (ºC) | 45.0063
| T_7 (ºC) | 185.2206
| P_1 (bar) | 4.6477
| P_2 (bar) | 92.9538
| P_3 (bar) | 92.9538
| P_4 (bar) | 91.0947
| P_5 (bar) | 4.8923
| P_6 (bar) | 4.6477
| P_7(bar) | 4.6477
| Power cycle mas flow rate (kg/s) | 641.496
| bypassing factor | 0.25
| UA recuperator (MW/K) | 47.0233
| UA SSG (MW/K) | 2.7049

## sCO2-RB
Sco2-RB
| PB main results |  | Cooling system main results
| Power generated (MW) | 86.2039 | Thermal power dissiped (MW) | 38.9548
| Thermal Power required (MW) | 125.1587 | Fan power consume (MW) | 2.5933
| efficiency (%) | 68.8757 | Air mass flow rate (kg/s) | 8151.0229
| T_1 (ºC) | 35 | Cooler UA factor (MW/K) | 12.0537
| T_2 (ºC) | 94.3261 | Air inlet temperature (ºC) | 25
| T_3 (ºC) | 269.9901 | Air outlet temperature (ºC) | 45
| T_3p (ºC) | 253.7628
| T_4 (ºC) | 391
| T_5 (ºC) | 272.9928
| T_6 (ºC) | 95.2306
| T_7 (ºC) | 213.6106
| P_1 (bar) | 80
| P_2 (bar) | 260
| P_3 (bar) | 260
| P_4 (bar) | 254.8
| P_5 (bar) | 84.2105
| P_6 (bar) | 80
| P_7(bar) | 80
| Power cycle mas flow rate (kg/s) | 1414.3007
| bypassing factor | 0.28
| UA recuperator (MW/K) | 49.713
| UA SSG (MW/K) | 14.2247